## Config (hidden)
Standard Code | Part | Revision
TEM 000329 | GL0 | 0
TITLE
TEM |  | English
TITLE | TITLE | Title | Título | Título | Título | Título
|  | SITES |  | BUSINESS
Title |  | CR | Corporate | 0 | All Business | Attributes Configuration
Standard Code |  | GL | Global | C | Compressors | Page
Revision |  | AM | Americas | E | Electronics | of
Part |  | EU | Europe
Wait |  | BR | Brazil
Cancel |  | CN | China
Microsoft Excel |  | IT | Italy
|  | MX | Mexico
|  | SK | Slovakia
|  | US | United States of America

## TEM 000329
UTILITIES AVAILABLE: |  |  | RELATED TO
a) Compressed air: |  |  |  | f) Drinking Water:
Low pressure compressed air |  | 6,5 bar ± 0.3 |  | Pressure / Temperature | N/A
High pressure compressed air |  | 16,5 bar ± 0.3 |  | g) Oil:
b) Steam: |  |  |  | Cooling oil | 5.0 bar at 30 ° C
Pressure |  | none |  | Cutting oil | 4,5-5.0 bar
c) Natural Gas: |  |  |  | Burnishing oil | 4,5-5.0 bar
Pipeline |  | 4 kPa, 10 KPa |  | Grinding oil in the generation point | 3,5-4,5 bar
Heat power |  | 34-36 MJ/m³ |  | h) Filters:
d) Cooling water: |  |  |  | Grinding machine | 40μm
Maximum pressure in the pipeline |  | 3.0 bar |  | Buffering (polishing) | 5μm
Return pressure |  | 1.5 bar |  | i) Power supply:
Speed |  | TBD |  | Grounding System | TN-S
Feeding temperature |  | 10 °C |  | Voltage Levels | 220-Single Phase and 400-Three Phase
Return temperature |  | 16 °C
e) Industrial Water:
Pressure / Temperature |  | N/A |  | Frequency | 50 Hz
MACHINE/EQUIPMENT ESTIMATED COMSUMPTION VALUES AND INSTALLATION DETAILS:
Filled by supplier
Compressed Air |  |  |  | Steam
Consumption (Nm³/min) |  |  |  | Consumption (L/min)
Working Pressure (bar) |  |  |  | Working Pressure (bar)
Cooling Water |  |  |  | Working Temperature (ºC)
Consumption (L/min) |  |  |  | Electrical Energy
Working Pressure (bar) |  |  |  | Supply Voltage (V) :
Working Temperature (ºC) |  |  |  | Phases: | Single-Phase
Industrual Water |  |  |  |  | Two-Phase
Consumption (L/min) |  |  |  |  | Three-Phase
Working Pressure (bar) |  |  |  | Frequency (Hz):
Working Temperature (ºC) |  |  |  | Rated Power (Kva):
Waste |  |  |  | Rated current (A):
Effluent Characteristics: |  | Oil |  | Maximum Load (A):
|  | Oil Free |  | IT Infrastructure | Yes
Disposal Volume (m³) |  |  |  |  | No
Gas |  |  |  | Cooling Oil:
Type of Gas: | Argon | Natural |  | Type of Cooling Oil: |  | Burnishing
| Helium | Hydrogen |  |  |  | Grinding
| Others | Nitrogen |  |  |  | Cut
Consumption (Nm³/min) | [5 empty] | Stamping
Working Pressure (bar) | [5 empty] | Lubricant
Dry Air | [5 empty] | Others
Consumption (Nm³/min) |  |  |  | Working Pressure (bar)
Working Pressure (bar) |  |  |  | Consumption (L/min)
MACHINE/EQUIPMENT REGISTRATION DATA:
Filled by the Responsable Specialist for Machine / Equipment Acquisition
Applicant |  |  |  | Date:
Machine / Equipment Denomination
General Data
Estimated Arrival |  |  |  | Supplier
Acquisition Date |  |  |  | Acquisition Value
Dimensions / Size |  |  |  | Weight (Kg)
Location
Line
Fixed Asset |  | Superior Machine / Equipment
Supplier Data
Country |  |  | Manufacturer
Serial Number |  |  | Type (Model)
Warranty
Warranty Start |  |  | Warranty End
MAINTENANCE CONTROL DATA:
Filled by Maintenance Enginnering
Planner Center
Cost Center
Responsable Work Center
ABC Denomination
Planner Group
Object Type
Machine Grounding Measurement (ohms) According to SOP 014503
In Service Since
Other Specific Information

## Data
| BR | MX | IT | SK | CN
a) Compressed air:
Low pressure compressed air | 5.0 bar ± 0.5 | 7.0 bar ± 0.2 | 6,4 bar ± 0.7 | 6,5 bar ± 0.3 | 6.5 bar ± 0.5 | BRAZIL
High pressure compressed air | 15.0 bar | 18.0 bar ± 0,5 | 12 bar ± 1 | 16,5 bar ± 0.3 | 18.0 bar ± 0.5 | MEXICO
b) Steam: | [5 empty] | ITALY
Pressure | 6.0 bar | 7.0 bar | 3.5 bar ± 0.5 | none | 5.5 bar ± 0.5 | SLOVAKIA
c) Natural Gas: | [5 empty] | CHINA
Pipeline | 2.0 bar at 30 °C | 2.0 bar at 30 °C | 1,5 bar at 30 °C | 4 kPa, 10 KPa | 10 KPa at 20 °C | 4
Heat power | 9065 kcal/Nm³ | 36.5 MJ/m³ | 36-38 MJ/m³ | 34-36 MJ/m³ | Min: 8400 kcal/Nm³ Max: 9300 Kcal/Nm³
d) Cooling water:
Maximum pressure in the pipeline | 3.0 bar | 4.5 bar | 2,8 bar | 3.0 bar | 4.5 bar
Return pressure | 1.5 bar | 1.5 bar | 1,5 bar | 1.5 bar | 2 bar
Speed | 2 to 3 m/s | 2 to 3 m/s | 1,2 to 2,4 m/s | TBD | 2 to 3 m/s
Feeding temperature | 29.5 to 30 °C | 30 °C | 18 °C | 10 °C | 32 °C
Return temperature | 35 °C (maximum) | 35 °C (maximum) | 30 °C (maximum) | 16 °C | 42 °C
e) Industrial Water:
Pressure / Temperature | 2.0 bar at 30 °C | 2.0 bar at 30 °C | 2.5 bar at 18 °C | N/A | 3.0 bar at 20 °C
f) Drinking Water:
Pressure / Temperature | 3.5 bar at 25ºC | 3.0 bar at 25ºC | 3.0 bar at 25ºC | 4.5 bar at 10°C | 3.0 bar at 20 ºC
g) Oil:
Cooling oil | 5.0 bar at 30 ° C | TBD | TBD | 5.0 bar at 30 ° C | TBD
Cutting oil | 5.0 bar | 5.8 bar | TBD | 4,5-5.0 bar | 4.8 bar
Burnishing oil | 4.0 bar | 4.4 bar | TBD | 4,5-5.0 bar | TBD
Grinding oil in the generation point | 5 ± 0,5 bar | 5.6 bar | 5 bar | 3,5-4,5 bar | 4.8 bar
h) Filters:
Grinding machine | 40μm | 34 g/m2 | 40um | 40μm | 40um
Buffering (polishing) | 5μm | 51 g/m2 | TBD | 5μm | 5um
i) Power supply:
Grounding System | TN-S | TN-S | TN-S | TN-S | TN-S
Voltage Levels | 220-Single Phase and 380-Three Phase | 127-Single Phase 220-Two Phase 277-For lighting 480-Three Phase | 220-Single Phase and 400-Three Phase | 220-Single Phase and 400-Three Phase | 220-Single Phase and 380-Three Phase
Frequency | 60 Hz | 60 Hz | 50 Hz | 50 Hz | 50 Hz